## Table 1
name | standby | alarm | ledCost | type
626-001 (Input Module, Single Input) | 0.5 | 2.1 | 1 | IO module
626-002 (Input/Output Module, Single Input/Output) | 0.5 | 3.8 | 1 | IO module
626-003 (Input Module, Twin Inputs) | 0.7 | 2.3 | 1 | IO module
626-004 (Input/Output Module, Twin Input/Outputs) | 0.7 | 4 | 1 | IO module
626-005 (Input Module, Single Input, Isolator) | 0.5 | 2.1 | 1 | IO module
626-006 (Input/Output Module, Single Input/Output, Isolator) | 0.5 | 3.8 | 1 | IO module
626-007 (Input Module, Twin Inputs, Isolator) | 0.7 | 2.3 | 1 | IO module
626-008 (Input/Output Module, Twin Input/Outputs, Isolator) | 0.7 | 4 | 1 | IO module
626-009 (Mains Switching Input/Output Module) | 0.5 | 3.8 | 1 | IO module
626-010 (Mains Switching Input/Output Module, Isolator) | 0.5 | 3.8 | 1 | IO module
626-011 (Mains Switching Input/Output Module, Twin Input/Outputs) | 0.7 | 4 | 1 | IO module
626-012 (Mains Switching Input/Output Module, Twin Input/Outputs, Isolator) | 0.7 | 4 | 1 | IO module
600-001 (Smoke/Heat Detector) | 0.26 | 2 | 1 | Detector
600-002 (Smoke/Heat Detector, Remote LED Output) | 0.26 | 5 | 1 | Detector
600-003 (Smoke Detector) | 0.26 | 2 | 1 | Detector
600-004 (Smoke Detector, Remote LED Output) | 0.26 | 5 | 1 | Detector
600-005 (Heat Detector) | 0.26 | 2 | 1 | Detector
600-006 (Heat Detector, Remote LED Output) | 0.26 | 5 | 1 | Detector
SNA-360-C2 (Smoke/Heat Detector) | 0.46 | 2 | 1 | Detector
SNA-360-CL (Smoke/Heat Detector, Remote LED Output) | 0.46 | 5 | 1 | Detector
SNA-360-S2 (Smoke Detector) | 0.46 | 2 | 1 | Detector
SNA-360-SL (Smoke Detector, Remote LED Output) | 0.46 | 5 | 1 | Detector
HNA-360-H2 (Heat Detector) | 0.46 | 2 | 1 | Detector
HNA-360-HL (Heat Detector, Remote LED Output) | 0.46 | 5 | 1 | Detector
660-001 (Manual Call Point) | 0.4 | 2 | 1 | MCP
660-005 (Manual Call Point, with Isolator) | 0.6 | 2 | 1 | MCP
620-001 (Mini Input Module, Single Detector Input) | 1 | 12 | 1 | IO module
620-002 (Mini Input Module, Single Contact Input) | 1 | 12 | 1 | IO module
620-003 (Mini Output Module, Single Output) | 1 | 12 | 0 | IO module
620-004 (Mini Input Module, Detector Input, without Enclosure) | 1 | 12 | 1 | IO module
621-001 (Input Module, Single Input Monitored) | 0.4 | 3 | 1 | IO module
621-002 (Input/Output Module, Single Input/Output, with Output Relay) | 0.4 | 3 | 1 | IO module
621-003 (Alarm Zone Input Module, Loop Powered) | 1 | 25 | 4 | IO module
621-004 (Alarm Zone Input Module, Externally Powered) | 0.5 | 1.2 | 4 | IO module
621-005 (Input Module, Isolator Monitored Input) | 0.7 | 2 | 1 | IO module
621-006 (Input/Output Module, Isolator, with Output Relay) | 0.7 | 2 | 1 | IO module
621-007 (Input Module, Single Input, Switched External DC Supply) | 0.65 | 2 | 1 | IO module
622-001 (LSM, Audio/Visual Alarm Control Module) | 0.65 | 1.5 | 4 | IO module
680-001 (Loop Isolator) | 0.6 | 5 | 1 | IO module
640-001 (Sounder, Audible Alarm, Red) | 0.65 | 8 | 0 | Sounder
640-002 (Sounder, Visual Alarm/Audio Alarm Device, White) | 0.65 | 5 | 0 | Sounder
640-003 (Sounder, Audible/Visual Alarm/Visual Alarm Device, Red) | 0.65 | 10 | 0 | Sounder
640-004 (Sounder, Audible/Visual Alarm Device, Red/White) | 0.65 | 10 | 0 | Sounder
641-001 (Sounder, Audible Alarm) | 0.35 | 13 | 0 | Sounder
641-002 (Sounder, Audible Alarm, Weatherproof) | 0.35 | 13 | 0 | Sounder
641-003 (Sounder, Visual Alarm) | 0.35 | 5 | 0 | Sounder
641-004 (Sounder, Visual Alarm, Weatherproof) | 0.35 | 5 | 0 | Sounder
641-005 (Sounder, Audible/Visual Alarm) | 0.35 | 16 | 0 | Sounder
641-006 (Sounder, Audible/Visual Alarm, Weatherproof) | 0.35 | 16 | 0 | Sounder

## Source References
Index | Reference
1 | 31-0149-r02_626_input_module.pdf
2 | 34-0001_r01_Catalogue_2026.pdf
3 | 31-0150-r02_626_input_output_module.pdf
4 | 31-0024-r05_600_smoke_heat_detector.pdf
5 | 31-0025-r05_600_smoke_detector.pdf
6 | 31-0026-r05_600_heat_detector.pdf
7 | 31-0042-r04_SNA-360_smoke_heat_detector.pdf
8 | 31-0043-r05_SNA-360_smoke_detector.pdf
9 | 31-0040-r04_HNA-360_heat_detector.pdf
10 | 31-0032-r08_660_manual_call_point.pdf
11 | 31-0027-r06_620_input_module.pdf
12 | 31-0028-r07_620_output_module.pdf
13 | 31-0029-r07_621_input_module.pdf
14 | 31-0030-r06_621_input_output_module.pdf
15 | 31-0031-r06_621_zone_input_module.pdf
16 | 31-0061-r02_622_A_V_alarm_control_module.pdf
17 | 31-0033-r06_680_loop_isolator.pdf
18 | 31-0051-r08_640_audio_visual_alarm.pdf
19 | 31-0074-r02_641_audio_visual_alarm.pdf